Specification

1.0 General

1.1 - Air filters classified as 99.99% or 99.999% efficient shall be absolute grade HEPA filters consisting of pleated media packs assembled in a V-bank configuration, polyurethane sealant, anodized aluminum enclosure and

seamless sealing gasket.

1.2 - Sizes shall be as noted on enclosed drawings or other supporting materials.

2.0 Construction

2.1 - Filter media shall be microfiber glass formed into mini-pleat, pleat-in-pleat V-bank design.

2.2 - The media packs shall be potted into the enclosing frame with fire retardant polyurethane sealant.

2.3 - An enclosing frame of anodized extruded aluminum shall form a rugged and durable enclosure.

2.4 - A poured-in-place sealing gasket shall be included on the downstream side of the enclosing frame to form a positive seal upon installation.

3.0 Performance

3.1 - Filter efficiency at 0.3 microns shall be (99.99% or 99.999%) when evaluated according to IEST-RP-CC007 for global efficiency. Each filter shall have a machine-printed label indicating the tested airflow, initial airflow resistance, and efficiency values. Note: 95% units are not scan tested.

3.2 - Initial resistance shall be 1.2” w.g. ±15% target at rated airflow. (0.50” w.g. for 95%)*.

3.3 - Filter shall be qualified as UL 586 and UL 900 per Underwriters Laboratories.

3.4 - Manufacturer shall provide evidence of facility certification to ISO 9001:2015.

Filters shall be Camfil Filtra 2000 with gasket seal or equivalent.

* Items in parentheses ( ) require selection

October/2025